## Sheet1
Sharky 775 1.5 m3/hr, DN20, Kv = 5.48
Flow rate	m3/hr	1.5	1.25	1	0.75	0.5
	Lit/min	25.0	20.8	16.7	12.5	8.3
Pressure required	Bar	0.07	0.05	0.03	0.02	0.01
	M head	0.76	0.53	0.34	0.19	0.08

Sharky 775 2.5 m3/hr, DN20, Kv = 7.91
Flow rate	m3/hr	2.5	2	1.5	1	0.5
	Lit/min	41.7	33.3	25.0	16.7	8.3
Pressure required	Bar	0.100	0.064	0.036	0.016	0.004
	M head	1.02	0.65	0.37	0.16	0.04

Kamstrup 302 1.5 m3/hr, DN15, Kv = 4.89
Flow rate	m3/hr	1.5	1.25	1	0.75	0.5
	Lit/min	25.0	20.8	16.7	12.5	8.3
Pressure required	Bar	0.09	0.07	0.04	0.02	0.01
	M head	0.96	0.67	0.43	0.24	0.11

Kamstrup 302 2.5 m3/hr, DN20, Kv = 8.15
Flow rate	m3/hr	2.5	2	1.5	1	0.5
	Lit/min	41.7	33.3	25.0	16.7	8.3
Pressure required	Bar	0.094	0.060	0.034	0.015	0.004
	M head	0.96	0.61	0.35	0.15	0.04

Kamstrup 402 1.5 m3/hr, Kv = 3
Flow rate	m3/hr	1.5	1.25	1	0.75	0.5
	Lit/min	25.0	20.8	16.7	12.5	8.3
Pressure required	Bar	0.25	0.174	0.111	0.063	0.028
	M head	2.55	1.77	1.13	0.64	0.28

Kamstrup 402 2.5 m3/hr, Kv = 13.5
Flow rate	m3/hr	2.5	2	1.5	1	0.5
	Lit/min	41.7	33.3	25.0	16.7	8.3
Pressure required	Bar	0.034	0.022	0.012	0.005	0.001
	M head	0.35	0.22	0.13	0.06	0.01

Sontex Superstatic 440 1.5 m3/hr, DN20, Kv = 5
Flow rate	m3/hr	1.5	1.25	1	0.75	0.5
	Lit/min	25.0	20.8	16.7	12.5	8.3
Pressure required	Bar	0.09	0.063	0.040	0.023	0.010
	M head	0.92	0.64	0.41	0.23	0.10

Sontex Superstatic 440 2.5 m3/hr, DN20, Kv = 5
Flow rate	m3/hr	2.5	2	1.5	1	0.5
	Lit/min	41.7	33.3	25.0	16.7	8.3
Pressure required	Bar	0.25	0.160	0.090	0.040	0.010
	M head	2.55	1.63	0.92	0.41	0.10

Sontex Superstatic 440 3.5 m3/hr, DN25, Kv = 8.75
Flow rate	m3/hr	3.5	2.5	1.5	1	0.5
	Lit/min	58.3	41.7	25.0	16.7	8.3
Pressure required	Bar	0.16	0.082	0.029	0.013	0.003
	M head	1.63	0.83	0.30	0.13	0.03

Qalcosonic E3 1.5 m3/hr, DN20, Kv = 6.23
Flow rate	m3/hr	1.5	1.25	1	0.75	0.5
	Lit/min	25.0	20.8	16.7	12.5	8.3
Pressure required	Bar	0.058	0.040	0.026	0.014	0.006
	M head	0.59	0.41	0.26	0.15	0.07

Qalcosonic E3 2.5 m3/hr, DN20, Kv = 8.15
Flow rate	m3/hr	2.5	2	1.5	1	0.5
	Lit/min	41.7	33.3	25.0	16.7	8.3
Pressure required	Bar	0.094	0.060	0.034	0.015	0.004
	M head	0.96	0.61	0.35	0.15	0.04

Qalcosonic E3 3.5 m3/hr, DN25, Kv = 17.5
Flow rate	m3/hr	3.5	2.5	1.5	1	0.5
	Lit/min	58.3	41.7	25.0	16.7	8.3
Pressure required	Bar	0.04	0.020	0.007	0.003	0.001
	M head	0.41	0.21	0.07	0.03	0.01

Sika VVX20 2-40 lit/min, Kv = 4.62
Flow rate	m3/hr	2.4	1.8	1.2	0.6	0.3
	Lit/min	40.0	30.0	20.0	10.0	5.0
Pressure required	Bar	0.27	0.152	0.067	0.017	0.004
	M head	2.75	1.55	0.69	0.17	0.04

Sika VVX20 5-80 lit/min, Kv = 9.6
Flow rate	m3/hr	4.8	3.6	2.4	1.2	0.6
	Lit/min	80.0	60.0	40.0	20.0	10.0
Pressure required	Bar	0.25	0.141	0.063	0.016	0.004
	M head	2.55	1.43	0.64	0.16	0.04

	Pressure causing energy waste and/or limiting flowrate
	For many systems, pressure a bit too high / not ideal
	Reasonable
	Good low pressure for most systems
Note – this is only our opinion. Circumstance will affect requirements.